## No Project Name - Inputs
MCHEDesigner: | 2026-09-04 13:42:09
Version: | 1.2.5.6
Project Description:
Micro Channel Heat Exchanger
Solver Type | MicroChannel
Tube Thermal Conductivity | 237 | W/m K
Fin Thermal Conductivity | 237 | W/m K
Tube Surface Roughness | 0 | m
Microchannel Parameters
Number of Banks (In direction of Air Flow) | 1
Number of Tubes per Bank | 118
Number of Segments | 20
Tube Length | 2063 | mm
Tube Height | 2 | mm
Tube Width | 32 | mm
Tube Vertical Spacing | 10.1 | mm
Bank Horizontal Spacing | 0 | m
Ports Per Tube | 25
Port Type | Rectangular
Port Width | 0.859 | mm
Port Height | 1.36 | mm
Fin Parameters
Fin Type | Louver Fin
Fins Per Inch | 21
Fin Spacing | 1.1295 | mm
Fin Thickness | 0.08 | mm
Louver Pitch | 1.1 | mm
Louver Length | 7 | mm
Louver Angle | 27 | degree
Louver Square-V Flat Width | 5e-05 | m
Louver Square-V Inside Radius | 1e-05 | m
Louver Square-V Half-Angle | 15 | degree
Louver Count | 26
Heat Transfer Correlations
Air Side HTC
Correlation Type | Builtin
Correlation | LouverFin:KimBullurd(Dry)
Correction Factor | 1
Refrigerant Liquid Phase
Correlation Type | Builtin
Correlation | Gnielinski
Correction Factor | 1
Refrigerant Two Phase
Correlation Type | Builtin
Correlation | Con: Dobson
Correction Factor | 1
Refrigerant Vapor Phase
Correlation Type | Builtin
Correlation | Gnielinski
Correction Factor | 1
Pressure Drop Correlations
Air Side Pressure Drop
Correlation Type | Builtin
Correlation | LouverFin:SanHua(Dry,CFDBased)
Correction Factor | 1
Refrigerant Liquid Phase
Correlation Type | Builtin
Correlation | Churchill
Correction Factor | 1
Refrigerant Two Phase
Correlation Type | Builtin
Correlation | Fridel
Correction Factor | 1
Refrigerant Vapor Phase
Correlation Type | Builtin
Correlation | Churchill
Correction Factor | 1
Material Properties
Material Properties
Tube Density | 2700 | kg/m3
Tube Material Price | 0 | RMB/kg
TubesAreRifled | 0
Tube Surface Roughness | 0 | m
Tube Thermal Conductivity | 237 | W/mK
Fin Material Density | 2700 | kg/m3
Fin Material Price | 0 | RMB/kg
Fin Thermal Conductivity | 237 | W/mK
Fouling Resistance | 0 | m2K/W
Refrigerant Price | 0
Cost Library Path
Header Info
Header Number | Type | Input Parameter | State Parameter | Mass Flow Rate [kg/s] | UpStream Tubes | Downstream Tubes | Header Inner Diameter [m] | Connecting Tube ID [m] | Connecting Tube Length [m]
1 | Inlet | SinglePhasePT | P= 1377.0 kPa, T= 55 ℃ | 0.6525 |  | 1-94 | 0 | 0 | 0
2 | Intermediate |  |  | 0.6525 | 1-94 | 95-118 | 0 | 0 | 0
3 | Outlet |  |  | 0.6525 | 95-118 |  | 0 | 0 | 0
Air Inlet Conditions
Air Inlet Temperature [℃]
| Segment-1 | Segment-2 | Segment-3 | Segment-4 | Segment-5 | Segment-6 | Segment-7 | Segment-8 | Segment-9 | Segment-10 | Segment-11 | Segment-12 | Segment-13 | Segment-14 | Segment-15 | Segment-16 | Segment-17 | Segment-18 | Segment-19 | Segment-20
Tube-1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-4 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-6 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-8 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-9 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-11 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-12 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-13 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-14 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-15 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-16 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-18 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-19 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-21 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-22 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-26 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-27 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-28 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-29 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-31 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-32 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-33 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-37 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-38 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-39 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-40 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-42 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-43 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-44 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-45 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-46 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-47 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-48 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-49 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-50 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-51 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-52 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-53 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-56 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-57 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-58 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-59 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-60 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-61 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-62 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-63 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-64 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-65 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-66 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-67 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-68 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-69 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-71 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-72 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-73 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-74 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-75 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-76 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-77 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-78 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-79 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-80 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-81 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-82 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-83 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-84 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-85 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-86 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-87 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-88 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-89 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-90 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-91 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-92 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-93 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-94 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-95 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-96 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-97 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-98 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-99 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-100 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-101 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-102 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-103 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-104 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-105 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-106 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-107 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-108 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-109 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-110 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-111 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-112 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-113 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-114 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-115 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-116 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-117 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Tube-118 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Air Inlet Velocity [m/s]
| Segment-1 | Segment-2 | Segment-3 | Segment-4 | Segment-5 | Segment-6 | Segment-7 | Segment-8 | Segment-9 | Segment-10 | Segment-11 | Segment-12 | Segment-13 | Segment-14 | Segment-15 | Segment-16 | Segment-17 | Segment-18 | Segment-19 | Segment-20
Tube-1 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-2 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-3 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-4 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-5 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-6 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-7 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-8 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-9 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-10 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-11 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-12 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-13 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-14 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-15 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-16 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-17 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-18 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-19 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-20 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-21 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-22 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-23 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-24 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-25 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-26 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-27 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-28 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-29 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-30 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-31 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-32 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-33 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-34 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-35 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-36 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-37 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-38 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-39 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-40 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-41 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-42 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-43 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-44 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-45 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-46 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-47 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-48 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-49 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-50 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-51 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-52 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-53 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-54 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-55 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-56 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-57 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-58 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-59 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-60 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-61 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-62 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-63 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-64 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-65 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-66 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-67 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-68 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-69 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-70 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-71 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-72 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-73 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-74 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-75 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-76 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-77 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-78 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-79 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-80 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-81 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-82 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-83 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-84 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-85 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-86 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-87 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-88 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-89 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-90 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-91 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-92 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-93 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-94 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-95 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-96 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-97 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-98 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-99 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-100 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-101 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-102 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-103 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-104 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-105 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-106 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-107 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-108 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-109 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-110 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-111 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-112 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-113 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-114 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-115 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-116 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-117 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Tube-118 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054 | 2.8054
Air Inlet RH[%]
| Segment-1 | Segment-2 | Segment-3 | Segment-4 | Segment-5 | Segment-6 | Segment-7 | Segment-8 | Segment-9 | Segment-10 | Segment-11 | Segment-12 | Segment-13 | Segment-14 | Segment-15 | Segment-16 | Segment-17 | Segment-18 | Segment-19 | Segment-20
Tube-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-4 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-6 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-7 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-11 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-12 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-13 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-14 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-15 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-17 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-18 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-19 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-21 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-22 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-23 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-25 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-26 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-27 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-28 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-29 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-31 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-33 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-34 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-36 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-42 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-43 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-44 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-45 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-46 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-47 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-48 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-49 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-50 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-51 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-52 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-53 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-54 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-56 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-57 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-58 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-59 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-61 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-62 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-63 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-64 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-65 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-66 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-67 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-68 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-69 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-70 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-71 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-72 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-73 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-74 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-75 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-76 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-77 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-78 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-79 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-80 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-81 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-82 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-83 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-84 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-85 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-86 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-87 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-88 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-89 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-90 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-91 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-92 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-93 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-94 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-95 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-96 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-97 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-98 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-99 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-100 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-101 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-102 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-103 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-104 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-105 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-106 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-107 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-108 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-109 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-110 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-111 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-112 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-113 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-114 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-115 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-116 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-117 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Tube-118 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40

## No Project Name - Results
MCHEDesigner
Local / UTC Time: | 2026-09-04 13:42:09
Version: | 1.2.5.6
Project Description:
Heat Loads
Total Heat Load | 96518.7147 | W
Sensible Heat Load | 96518.7147 | W
Latent Heat Load | 0 | W
Sensible Heat Ratio | 1
Ref. Liquid Heat Load | -5450.3742 | W
Ref. Two Phase Heat Load | -85872.4145 | W
Ref. Vapor Heat Load | -5195.926 | W
Ref. Abs. Heat Load Sum | 96518.7147 | W
Charge/Condensate
Total Refrigerant Charge | 1.8009 | kg
In-tube Ref. Liquid Charge | 0.50049 | kg
In-tube Ref. Two Phase Charge | 1.2799 | kg
In-tube Ref. Vapor Charge | 0.020533 | kg
Condensate | 0 | kg/s
Flow Rates
Total Refrigerant Flow Rate | 0.6525 | kg/s
Air Mass Flow Rate | 7.7775 | kg/s
Air Flow Rate | 6.9444 | m3/s
Standard Air Flow Rate | 6.7937 | m3/s
Pressure Drops
HX Air Side Pressure Drop | 0.093188 | kPa
System Air-Side Resistance | 0 | Pa
Total Air Side Pressure Drop | 0.093188 | kPa
Refrigerant Side Pressure Drop | 75.8187 | kPa
Refrigerant Saturation Temperature Drop | 2.3231 | °C
Outlet Conditions
Average Air Outlet Temperature | 47.04 | °C
Average Air Outlet Wetbulb Temperature | 26.938 | °C
Average Air Outlet RH | 21.125 | %
Average Refrigerant Outlet Pressure | 1301.1813 | kPa
Average Refrigerant Outlet Temperature | 43.273 | °C
Average Refrigerant Outlet Quality | -0.050234
Average Refrigerant Saturation Delta | -4.395 | °C
Heat Transfer
Primary Heat Transfer Area | 15.523 | m2
Secondary Heat Transfer Area | 112.5597 | m2
Total Air Side Heat Transfer Area | 128.0827 | m2
Refrigerant Side Heat Transfer Area | 27.009 | m2
Refrigerant Side Area Enhancement Factor | 1 | [-]
Coil Face Area | 2.4754 | m2
Average Fin Effectiveness | 0.92422
Average Air Side HTC | 146.69 | W/m2K
Average Refrigerant HTC | 3839.6454 | W/m2K
Average Refrigerant Liquid Phase HTC | 2674.0283 | W/m2K
Average Refrigerant Two-phase HTC | 4053.1509 | W/m2K
Average Refrigerant Vapor HTC | 1003.2244 | W/m2K
Refrigerant Phase Distribution
Liquid - % Coil Length | 6.7109 | %
Two Phase - % Coil Length | 89.3233 | %
Vapor - % Coil Length | 3.9658 | %
Heat Exchanger Material
Fin Material Volume | 0.0045263 | m3
Tube Material Volume | 0.0085616 | m3
Fin Material Mass | 12.2211 | kg
Tube Material Mass | 23.1164 | kg
Heat Exchanger Dimensions
Coil Length | 2063 | mm
Coil Depth | 32 | mm
Coil Height | 1199.9 | mm
Miscellaneous
ARI410 Ap | 0 | m2
ARI410 As | 0 | m2
Coil Cost(Simple) | 0 | $
Coil Cost(User Calculated) | 0 | $
Time Required | 0.5 | [s]
Iterations | 1 | [s]
Tube | Ref. M[kg/s] | Q_Total[W] | Q_Sen[W] | Q_Latent[W] | Avg. Ref HTC [W/m2 K] | Avg. Re | Tube Condensate [kg/s]
Tube 1 | 0.0069415 | -1029.88 | -1029.88 | 0 | 2986.58 | 9955.09 | 0
Tube 2 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 3 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 4 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 5 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 6 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 7 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 8 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 9 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 10 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 11 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 12 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 13 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 14 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 15 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 16 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 17 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 18 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 19 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 20 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 21 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 22 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 23 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 24 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 25 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 26 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 27 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 28 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 29 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 30 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 31 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 32 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 33 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 34 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 35 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 36 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 37 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 38 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 39 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 40 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 41 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 42 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 43 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 44 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 45 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 46 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 47 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 48 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 49 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 50 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 51 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 52 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 53 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 54 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 55 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 56 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 57 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 58 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 59 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 60 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 61 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 62 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 63 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 64 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 65 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 66 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 67 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 68 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 69 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 70 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 71 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 72 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 73 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 74 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 75 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 76 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 77 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 78 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 79 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 80 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 81 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 82 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 83 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 84 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 85 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 86 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 87 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 88 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 89 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 90 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 91 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 92 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 93 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 94 | 0.0069415 | -838.288 | -838.288 | 0 | 3817.71 | 12527.9 | 0
Tube 95 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 96 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 97 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 98 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 99 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 100 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 101 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 102 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 103 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 104 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 105 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 106 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 107 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 108 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 109 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 110 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 111 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 112 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 113 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 114 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 115 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 116 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 117 | 0.027187 | -724.493 | -724.493 | 0 | 3976.38 | 11200.3 | 0
Tube 118 | 0.027187 | -864.753 | -864.753 | 0 | 3588.1 | 10086 | 0
Outlet Tube States
| Pressure [Pa] | Temperature [K] | Quality/Mass Fraction | Saturation Delta [K] | Mass Flow Rate [kg/s]
Tube 95 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 96 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 97 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 98 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 99 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 100 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 101 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 102 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 103 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 104 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 105 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 106 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 107 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 108 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 109 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 110 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 111 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 112 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 113 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 114 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 115 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 116 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 117 | 1300820 | 316.565 | -0.048497 | -4.2419 | 0.027187
Tube 118 | 1309420 | 313.129 | -0.090276 | -7.9458 | 0.027187
Refrigerant Side Pressure [Pa]
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1377000 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1302170 | 1310760
SegNum-2 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1376040 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1303520 | 1312110
SegNum-3 | 1374600 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1374940 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1304870 | 1313460
SegNum-4 | 1373060 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1373390 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1306220 | 1314800
SegNum-5 | 1371550 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1371830 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1307570 | 1316150
SegNum-6 | 1370110 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1370310 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1308920 | 1317500
SegNum-7 | 1368760 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1368830 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1310480 | 1318850
SegNum-8 | 1367500 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1367410 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1312500 | 1320190
SegNum-9 | 1366330 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1366050 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1314820 | 1321540
SegNum-10 | 1365260 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1364760 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1317420 | 1322890
SegNum-11 | 1364280 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1363540 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1320270 | 1324340
SegNum-12 | 1363410 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1362380 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1323350 | 1326430
SegNum-13 | 1362630 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1361300 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1326650 | 1328930
SegNum-14 | 1361940 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1360280 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1330160 | 1331790
SegNum-15 | 1361350 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1359340 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1333870 | 1334980
SegNum-16 | 1360870 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1358460 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1337770 | 1338470
SegNum-17 | 1360490 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1357660 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1341860 | 1342250
SegNum-18 | 1360260 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1356920 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346130 | 1346310
SegNum-19 | 1360180 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1356250 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350580 | 1350620
SegNum-20 | 1360110 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355660 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190 | 1355190
Refrigerant Side Temperature [C]
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 51.685 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 52.449 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 43.715 | 40.227
SegNum-2 | 49.941 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 49.946 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 44.335 | 40.748
SegNum-3 | 49.895 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 49.906 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 44.996 | 41.319
SegNum-4 | 49.849 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 49.859 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 45.702 | 41.945
SegNum-5 | 49.805 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 49.812 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 46.455 | 42.631
SegNum-6 | 49.762 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 49.767 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 47.257 | 43.383
SegNum-7 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 49.723 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 47.933 | 44.205
SegNum-8 | 49.686 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 49.681 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 47.989 | 45.104
SegNum-9 | 49.652 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 49.641 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 48.056 | 46.086
SegNum-10 | 49.621 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 49.603 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 48.133 | 47.157
SegNum-11 | 49.592 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 49.567 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.217 | 48.317
SegNum-12 | 49.567 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 49.533 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.309 | 48.419
SegNum-13 | 49.545 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 49.501 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.407 | 48.49
SegNum-14 | 49.525 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 49.471 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.512 | 48.572
SegNum-15 | 49.509 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 49.443 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.623 | 48.665
SegNum-16 | 49.495 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 49.417 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.74 | 48.767
SegNum-17 | 49.486 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 49.394 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.862 | 48.878
SegNum-18 | 47.959 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 49.372 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.989 | 48.998
SegNum-19 | 45.686 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.353 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.122 | 49.125
SegNum-20 | 43.839 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.336 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26 | 49.26
Refrigerant Quality/Mass Fraction
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 1.0121 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | 1.0175 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.045356 | -0.087767
SegNum-2 | 0.95235 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | 0.97607 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.038829 | -0.08247
SegNum-3 | 0.88689 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | 0.92853 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.031797 | -0.076589
SegNum-4 | 0.82181 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | 0.88122 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.024224 | -0.070066
SegNum-5 | 0.75715 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | 0.83415 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.016074 | -0.06284
SegNum-6 | 0.69289 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | 0.78732 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.0073087 | -0.054841
SegNum-7 | 0.62904 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.74073 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | 0.001974 | -0.045997
SegNum-8 | 0.56562 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.69437 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | 0.011455 | -0.036226
SegNum-9 | 0.50264 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.64824 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | 0.020942 | -0.02544
SegNum-10 | 0.44012 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.60234 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | 0.030432 | -0.013546
SegNum-11 | 0.37809 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.55667 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | 0.039945 | -0.00055083
SegNum-12 | 0.31662 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.51122 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.049487 | 0.013078
SegNum-13 | 0.25577 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.466 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.05907 | 0.026848
SegNum-14 | 0.19566 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.42102 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.068702 | 0.040685
SegNum-15 | 0.13649 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.37627 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.078392 | 0.0546
SegNum-16 | 0.078552 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.33178 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.088147 | 0.068603
SegNum-17 | 0.023436 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.28755 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.097974 | 0.082708
SegNum-18 | -0.017989 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.24362 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.10788 | 0.096927
SegNum-19 | -0.044521 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.20001 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11787 | 0.11127
SegNum-20 | -0.065819 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.15678 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12796 | 0.12575
Air Side Temperature [C]
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 47.142 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 48.038 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 42.319 | 39.251
SegNum-2 | 47.688 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 47.903 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 42.841 | 39.676
SegNum-3 | 47.627 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 47.861 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 43.399 | 40.143
SegNum-4 | 47.56 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 43.995 | 40.654
SegNum-5 | 47.49 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 44.631 | 41.216
SegNum-6 | 47.418 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 47.698 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 45.309 | 41.831
SegNum-7 | 47.344 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 47.642 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 45.821 | 42.505
SegNum-8 | 47.266 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 47.587 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 45.985 | 43.242
SegNum-9 | 47.183 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 47.531 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 46.089 | 44.049
SegNum-10 | 47.094 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 47.475 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 46.193 | 44.93
SegNum-11 | 46.996 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 47.418 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 46.297 | 45.75
SegNum-12 | 46.885 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 47.36 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.404 | 46.091
SegNum-13 | 46.755 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 47.301 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.514 | 46.233
SegNum-14 | 46.596 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 47.239 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.627 | 46.366
SegNum-15 | 46.392 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 47.175 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.743 | 46.498
SegNum-16 | 46.11 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 47.106 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.862 | 46.629
SegNum-17 | 45.288 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 47.031 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.985 | 46.763
SegNum-18 | 40.781 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 46.947 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 47.111 | 46.899
SegNum-19 | 39.507 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 46.851 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.241 | 47.039
SegNum-20 | 38.753 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 46.739 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.375 | 47.182
Air Outlet RH %
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 21.0222 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 20.0874 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 26.9463 | 31.7084
SegNum-2 | 20.4471 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 20.2242 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 26.2195 | 30.9954
SegNum-3 | 20.51 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 20.2669 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 25.4677 | 30.2336
SegNum-4 | 20.5795 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 20.3213 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 24.6921 | 29.4222
SegNum-5 | 20.6521 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 20.3775 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 23.8939 | 28.5606
SegNum-6 | 20.7273 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 20.4344 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 23.0749 | 27.649
SegNum-7 | 20.8055 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 20.4917 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 22.4782 | 26.6883
SegNum-8 | 20.8877 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 20.5493 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 22.2899 | 25.68
SegNum-9 | 20.9751 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 20.6073 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 22.1717 | 24.6265
SegNum-10 | 21.0699 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 20.6658 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 22.0551 | 23.5314
SegNum-11 | 21.175 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 20.7251 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 21.9379 | 22.5629
SegNum-12 | 21.2947 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 20.7857 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 21.8188 | 22.1727
SegNum-13 | 21.4358 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 20.8482 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 21.6975 | 22.0131
SegNum-14 | 21.6093 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 20.9132 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.5734 | 21.8637
SegNum-15 | 21.8346 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 20.9818 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.4466 | 21.718
SegNum-16 | 22.1513 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.0553 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.3169 | 21.5731
SegNum-17 | 23.1554 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1356 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.1844 | 21.4272
SegNum-18 | 29.225 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.2253 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.0492 | 21.2795
SegNum-19 | 31.2769 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 21.3284 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 20.9111 | 21.1294
SegNum-20 | 32.5681 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 21.451 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.7705 | 20.9765
Refrigerant Local HTC [W/m2 K]
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 1226.08 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 1001.36 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2681.7 | 2626.14
SegNum-2 | 5469.74 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 5530.83 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2692.02 | 2634.38
SegNum-3 | 5264.01 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 5369.29 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2703.18 | 2643.51
SegNum-4 | 5045.23 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 5216.79 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2715.26 | 2653.62
SegNum-5 | 4817.66 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 5058.35 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2728.36 | 2664.82
SegNum-6 | 4582.81 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 4895.33 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2742.57 | 2677.25
SegNum-7 | 4341.26 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 4728.38 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2974.27 | 2691.06
SegNum-8 | 4093.12 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 4557.81 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 3368.46 | 2706.42
SegNum-9 | 3838.21 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 4383.77 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 3620.32 | 2723.54
SegNum-10 | 3576.14 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 4206.29 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 3852.22 | 2742.68
SegNum-11 | 3306.22 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4025.32 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 4070.97 | 2887.42
SegNum-12 | 3027.49 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 3840.73 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 4280.01 | 3473.26
SegNum-13 | 2738.52 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 3652.33 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 4481.55 | 3818.97
SegNum-14 | 2437.18 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 3459.85 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4677.05 | 4135.38
SegNum-15 | 2120.03 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 3262.95 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4867.62 | 4433
SegNum-16 | 1780.76 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 3061.17 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 5054.06 | 4717.15
SegNum-17 | 1099.42 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 2853.91 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 5237.02 | 4991.04
SegNum-18 | 343.206 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 2640.39 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5417.01 | 5256.81
SegNum-19 | 310.352 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 2419.52 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5594.38 | 5515.92
SegNum-20 | 314.219 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 2189.73 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64 | 5769.64
Local Condensate [kg/s]
| Tube 1 | Tube 2 | Tube 3 | Tube 4 | Tube 5 | Tube 6 | Tube 7 | Tube 8 | Tube 9 | Tube 10 | Tube 11 | Tube 12 | Tube 13 | Tube 14 | Tube 15 | Tube 16 | Tube 17 | Tube 18 | Tube 19 | Tube 20 | Tube 21 | Tube 22 | Tube 23 | Tube 24 | Tube 25 | Tube 26 | Tube 27 | Tube 28 | Tube 29 | Tube 30 | Tube 31 | Tube 32 | Tube 33 | Tube 34 | Tube 35 | Tube 36 | Tube 37 | Tube 38 | Tube 39 | Tube 40 | Tube 41 | Tube 42 | Tube 43 | Tube 44 | Tube 45 | Tube 46 | Tube 47 | Tube 48 | Tube 49 | Tube 50 | Tube 51 | Tube 52 | Tube 53 | Tube 54 | Tube 55 | Tube 56 | Tube 57 | Tube 58 | Tube 59 | Tube 60 | Tube 61 | Tube 62 | Tube 63 | Tube 64 | Tube 65 | Tube 66 | Tube 67 | Tube 68 | Tube 69 | Tube 70 | Tube 71 | Tube 72 | Tube 73 | Tube 74 | Tube 75 | Tube 76 | Tube 77 | Tube 78 | Tube 79 | Tube 80 | Tube 81 | Tube 82 | Tube 83 | Tube 84 | Tube 85 | Tube 86 | Tube 87 | Tube 88 | Tube 89 | Tube 90 | Tube 91 | Tube 92 | Tube 93 | Tube 94 | Tube 95 | Tube 96 | Tube 97 | Tube 98 | Tube 99 | Tube 100 | Tube 101 | Tube 102 | Tube 103 | Tube 104 | Tube 105 | Tube 106 | Tube 107 | Tube 108 | Tube 109 | Tube 110 | Tube 111 | Tube 112 | Tube 113 | Tube 114 | Tube 115 | Tube 116 | Tube 117 | Tube 118
SegNum-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SegNum-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0